GENTEC g- PROGWTM

USER MANUAL

For Area Alarms

2011

An Overview of Gentec g-ProgWTM                                     2

Selecting a Data Transferring (COM) Port                               3

Important Notes                                        3

Set Up COM Port Parameters                        3

Warning                                                   3

Hardware Setup for g-Smart Data Display™ System (Area Alarms)         4

Preparatory Work                                       4

Update System Firmware                               4

Start Running Gentec g-ProgWTM                                      5

Program Execution Procedure                          5

To Begin the Normal g-ProgW™ Session                  5

Standard Functions                                       8

Error Messages                                          8

Troubleshooting                                        9

Appendix                                                         10

Reset Device                                             10

RS-485 ID                                                 11

Device Mode of Switch S2                               12

An Overview of Gentec g-ProgW™ Software

Gentec g-ProgW™ is a Window-based program written specifically for the g-Local Data MasterTM (Master Alarm) and g-Smart Data Display EnhancedTM (Area Alarms) modules of Gentec Universal Process Monitoring and Control SystemTM to

- specify and upload their operating parameters, including

- the analog input channels and digital input ports in use;

- alarm-triggering upper and lower limits of analog channels and external events including, for example, remote switch statuses; and

- the actions of digital (TTL) outputs and/or relay switches in response to different alarm conditions.

Please note that, when g-Smart Data DisplayTM modules are used as subsystems of a g-Local Data MasterTM, there is no need to upload any operating parameters.

Standard PC serial communication ports, e.g. RS-232 COM or IEEE-485 ports, are used to transmit and receive control commands and data between the host computer and the modules.

Be sure to acquire and use only a genuine Gentec communication cable from Gentec Systems or its authorized agents. Do not use any

other look-alike cables from unknown sources. They may cause damages to the device or even the computer.

The user needs to know how to identify the communication port of the host computer in use. Other than this, most of the other operations are intuitive and self-explanatory with all complicated handshake and data transfer operations made transparent to the user.

The graphical user interface (GUI) of Gentec g-ProgW™ is very intuitive and easy to learn. Most, if not all, of the commands and functions are triggered or activated by clicking on-screen buttons or boxes. For more experienced computer users, many keyboard shortcuts are also available. Extensive error tracking is built in to minimize possible mistakes by the operators.

All setup and upgrade information can be saved and retrieved later for reviewing using the same program. It is highly recommended to keep and well-maintain these records as part of the system’s maintenance history.

Gentec g-ProgW™ is not a retail application program. It is normally distributed among authorized personnel of Gentec Systems and its agents. Any unauthorized use of the software is strictly prohibited. Gentec Systems reserves the right to take legal actions against any misuse of the software.

Selecting a Data Transferring (COM) Port

IMPORTANT NOTES

The flash memory on the module main board of both g-Local Data Master™ and g-Smart Data Display Enhanced™ can be read from or written to via their miniature RS-232 COM ports.

We have tested our software’s communication functions under various versions of Windows OS, including 2000, XP, and Vista. Several USB-to-232 cables have also been successfully tested under Windows.

For computers without any COM ports, use only reliable USB-to-232 converter cables and follow the procedures below. For first time users, please install the driver for the USB-to-232 cables before using g-ProgWTM.

Note that the COM port number assigned by the Windows OS may not be the same every time.

SET UP COM PORT PARAMETERS

Window XP, Vista, Win 7:

Follow the steps when initializing g-ProgWTM, the COM port will be set automatically. If not, click on Check COM button to check the COM number.

or:

Go to Control Panel | System and Maintenance | System | Device Manager| Ports (COM & LPT). You can see which COM port is being used.

WARNING

Unless all specified parameters match those of your system, g-ProgWTM will not be able to talk to

the module’s microprocessor.

Hardware Set Up For g-Smart Data Display Enhanced™ Modules (For Area Alarms)

PREPARATORY WORK

Hardware Requirement：

| Items | Quantity |
| --- | --- |
| PC or Notebook with either RS-232 or USB ports. | 1 |
| g-Smart Data Display EnhancedTM (for Area Alarms) | 1 |
| RS-232 Cable or USB-to-232 Cable | 1 |
| Gentec Communication Cable | 1 |
| Screwdriver (cross +) | 1 |

Hardware Setup Procedures:

- Make sure the power of g-Smart Data Display EnhancedTM is ON.

- Connect the RS-232 cable or USB-to-232 cable to the PC (Notebook).

- Connect the other end of the cable with Gentec communication cable.

- Remove the front plastic cover and data channel label on the right side of g-Smart Data Display EnhancedTM.

- Connect the Gentec communication cable to the RS-232 connector g-Smart Data Display EnhancedTM.

- Make sure Switch S2 is on RUN status with

only pin 5 and 6 ON or pin 1, pin 5, and pin

6 ON.

Note: Before to use, reset device after any change of SWITCH S2 (see APPENDIX: RESET DEVICE).

UPDATE SYSTEM FIRMWARE

System firmware will be uploaded in factory.

In case firmware needs to be uploaded,

contact a certified Gentec technician.

Start Running g-ProgWTM

PROGRAM EXECUTION PROCEDURES

For Window 2000, XP, please locate the executable file (gProgW2011.exe) and double click to execute. For Window Vista or Win 7, please right-click the executable file (gProgW2011.exe) and select “RUN AS ADMINISTRATOR” .

Please note that it is possible to run Gentec g-ProgW™ under most versions of Windows if

the graphic card of the host computer fully conforms to VESA 2.0 standards. Be sure to select a COM port that is not pre-occupied by the operating system. Check with Gentec Systems or its agents for the availability of Windows version of g-ProgW™.

TO BEGIN THE NORMAL g-ProgW™ SESSION

- The welcome screen.

- Unplug the GENTEC USB cable (connection between cable and computer) if already connected.

- Please plug in the GENTEC USB cable (connection between cable and computer) now.

Note: If your system is XP, g-ProgWTM will detect your COM port and setup it automatically.

Note: If your system is VISTA or Window 7, you may need to manually select the COM port number. (See SET UP COM PORT PARAMETERS)

Note: Com Port Error will stop after prompting message 3 times.

- Click on “Smart Data Display Enhanced” button to enter setup for area alarm.

- Main screen

- Set up the COM port number (see SET UP COM PORT PARAMETERS).

- Setup RS-485 ID if you know the number or click “ID Search” Button to Check RS-485 ID automatically.

- Keep Baud Rate at 19200.

- Click “Read” button to read parameters from g-Smart Data Display EnhancedTM.

- Click “CH0 Enable” or “CH1 Enable” button to enable/disable channel functions.

- Enter the Signal Range (e.g.: 4 to 20mA correspond to 1000 to 5000 mV).

- Enter the corresponding Physical Value (e.g.: 4mA corresponds to 0 psig, 20mA corresponds to 100 Psig on the transducer).

- Enter the Alarm high and low limit in physical value. (e.g.: 40 psig and 60 psig).

- Enter the Decimal Digits: digits after 0.

- Enter the Silence Time: length in minutes.

- Enter the Hysteresis: Usually keep factory setting 0.5%.

- Click “Write” button to change parameters of g-Smart Data Display EnhancedTM.

- Click “Read” button again to read parameters from g-Smart Data Display EnhancedTM.

- Make sure all parameters are correct.

STANDARD FUCTIONS

Open File: Open previously saved data.

Save File: Save data for future use.

Write: Write to Flash (Write the parameters on screen to flash memory of alarm module).

Read: Read from Flash (Read back the current parameters of alarm module connected).

ID Search: Search RS-485 ID for connected Area Alarm.

Check COM: Search COM port number for PC.

Note:

Com Port Error will stop automatically after prompting messages 3 times.

ERROR MESSAGES

| MESSAGES | PROBLEMS | SOLUTIONS |
| --- | --- | --- |
| Registry -> HARDWAREDEVICEMAPSERIALCOMM Not Found! | g-ProgW™ can not find COM PORT. | See SET UP COM PORT PARAMETERS solution |
| You have no COM Port to select. | No COM PORT in your PC | Use a PC or notebook with COM PORT |
| Response Error! | Return error form device | Try again or check Baud Rate and RS-485 ID |
| Device No Response! | No Response from device | Try again or check Baud Rate and RS-485 ID |
| Can not Find Device ID! | RS-485 ID not found | Check device power and RS-485 ID setup switch SW6 |

TROUBLESHOOTING

When encountering a problem, please first check the connections between:

- Gentec cable and mini communication port of Area Alarm

- USB-to-232 cable and Gentec cable

- USB-to-232 cable and computer.

Make sure:

- COM port number (for USB) is correct.

- RS-485ID is correct. (Dip Switch S6 in the back of PCB Panel). Typically, top module for channel 1 & 2, the address is 1. Second module for channel 3 & 4, the address is 2.

APPENDIX

RESET DEVICE

There are three ways to reset device.

- POWER switch:

- Remove the plastic caps and the fastening screws at the upper edge of the system and swing the module assembly to its horizontal position.

- Change to OFF position than switch to ON position of POWER switch S1.

- RESET button:

- Remove the plastic caps and the fastening screws at the upper edge of the system and swing the module assembly to its horizontal position.

- Press the RESET button S3 of g-Smart Data Display EnhancedTM.

- SUSPEND/TEST button:

Push SUSPEND/TEST button more than 10 seconds then release the button, the device will reset automatically.

RS-485 ID

There are three ways to check RS-485 ID.

- SWITCH SW 6:

- Remove the plastic caps and the fastening screws at the upper edge of the system and swing the module assembly to its horizontal position.

- SWITCH SW 6 determines the unique device ID for each g-Smart Data Display EnhancedTM module.

| Device ID | SW 6 DIP ON/OFF Setup |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| 001 | ON | OFF | OFF | OFF | OFF | OFF | OFF | OFF |
| 002 | OFF | ON | OFF | OFF | OFF | OFF | OFF | OFF |
| 003 | ON | ON | OFF | OFF | OFF | OFF | OFF | OFF |
| 004 | OFF | OFF | ON | OFF | OFF | OFF | OFF | OFF |
| 005 | ON | OFF | ON | OFF | OFF | OFF | OFF | OFF |
| 006 | OFF | ON | ON | OFF | OFF | OFF | OFF | OFF |
| 007 | ON | ON | ON | OFF | OFF | OFF | OFF | OFF |
| 008 | OFF | OFF | OFF | ON | OFF | OFF | OFF | OFF |
| … … … |  |  |  |  |  |  |  |  |
| 254 | OFF | ON | ON | ON | ON | ON | ON | ON |
| 255 | ON | ON | ON | ON | ON | ON | ON | ON |

- SWITCH S2:

- Set SWITCH S2 all pins to OFF.

| S2 SWITCH SETTING |  |  |  |  |  |  |  | OPERATIONAL MODE SELECTION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| X | X | X | X | OFF | OFF | OFF | OFF | Self test Mode |

- Push SUSPEND/TEST button more than 10 seconds then release button to reset device.

- The Seven Segment LED on the device will show information continuously as following order:

| LEFT Seven Segment LED | RIGHT Seven Segment LED |
| --- | --- |
| RS-485 ID | Baud Rate |
| Voltage of left channel | Voltage of right channel |
| Seven Segment all OFF | Seven Segment all OFF |
| Seven Segment all ON | Seven Segment all ON |

- g-ProgW™:

Click “ID Search” button to find device ID.

DEVICE MODE of SWITCH S2

Note: Reset Device (see RESET DEVICE) after any change of SWITCH S2.

| S2 SWITCH SETTING |  |  |  |  |  |  |  | OPERATIONAL MODE SELECTION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| X | X | X | X | OFF | OFF | OFF | OFF | Self test Mode(1) |
| X | X | X | X | ON | OFF | OFF | OFF | Measurement Mode(2) |
| X | X | X | X | OFF | ON | OFF | OFF | Unused |
| X | OFF | OFF | X | ON | ON | OFF | OFF | Run Mode(factory setting)(3) |
| X | X | X | X | OFF | OFF | ON | OFF | Calibration Mode |
| X | OFF | OFF | X | ON | OFF | ON | OFF | Run Mode with suspend 30 min.(4) |
| X | OFF | OFF | X | OFF | ON | ON | OFF | Run Mode with suspend 60 min.(5) |
| X | OFF | OFF | X | ON | ON | ON | OFF | Demo Mode |
| X | X | X | ON | X | X | X | OFF | Baud Rate 9600 |
| X | X | X | OFF | X | X | X | OFF | Baud Rate 19200 |
| X | X | X | X | X | X | X | ON | Firmware Update |

- All LED and buzzer will ON/OFF continuously.

- Show mV from input terminals.

- Suspend time set by Gentec g-ProgW™. Also, set pin2 ON will close channel left, set pin3 ON will close channel right.

- Suspend time set 30 minutes. Also, set pin2 ON will close channel left, set pin3 ON will close channel right.

- Suspend time set 60 minutes. Also, set pin2 ON will close channel left, set pin3 ON will close channel right.